

BUILDING WIRE SINGLE CORE Aluminium

CONDUIT

00363

## APPLICATION

For separate earth conductors, For switchboard and control

panel wiring. For fixed wiring within other enclosures or apparatus where the cable is not accessible without the use of tools.

**STANDARD** AS/NZS 5000.1

**VOLTAGE** 600/1000V

**CONDUCTOR** Aluminium 1 - 630mm2

**INSULATION** PVC, V-90

See below for

colour options

**MAX. OPERATING TEMP.** 90**°**C

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ***Item Number*** | ***Conductor*** | | ***Overall Diameter*** | | ***Nominal Diameter*** | ***Minimum Insulation Thickness*** | ***Approx. Mass*** | ***Minimum Installed Bending Radius*** |
|  | ***mm2*** | ***(No./mm)*** | ***Minimum (mm)*** | ***Maximum (mm)*** | ***mm*** | ***mm*** | ***Kg/Km*** | ***mm*** |
| DC18y/AL | 16 | 7/1.70 | 7.2 | 7.4 | 5.1 | 1 | 180 | 45 |
| DC19y/AL | 25 | 19/1.35 | 9.25 | 9.45 | 6.75 | 1.2 | 285 | 60 |
| DC110y/AL | 35 | 19/1.53 | 10.15 | 10.35 | 7.65 | 1.2 | 370 | 65 |
| DC111y/AL | 50 | 19/1.78 | 11.8 | 12 | 8.9 | 1.4 | 515 | 70 |
| DC112y/AL | 70 | 19/2.14 | 13.6 | 13.8 | 10.7 | 1.4 | 730 | 80 |
| DC113y/AL | 95 | 37/1.78 | 15.76 | 16 | 12.5 | 1.6 | 980 | 90 |
| DC1149y/AL | 120 | 37/2.03 | 17.51 | 17.75 | 14.21 | 1.6 | 1250 | 100 |
| DC115y/AL | 150 | 37/2.25 | 19.45 | 19.7 | 15.75 | 1.8 | 1500 | 110 |
| DC116y/AL | 185 | 37/2.52 | 21.74 | 22 | 17.64 | 2 | 1750 | 120 |
| DC117y/AL | 240 | 61/2.25 | 24.75 | 25.05 | 20.25 | 2.2 | 2200 | 130 |
| DC118y/AL | 300 | 61/2.52 | 27.58 | 27.9 | 22.68 | 2.4 | 2890 | 140 |
| DC119y/AL | 400 | 61/2.85 | 30.95 | 31.35 | 25.65 | 2.6 | 3530 | 150 |
| DC1110y/AL | 500 | 61/3.20 | 34.5 | 34.9 | 28.8 | 2.8 | 4450 | 160 |
| DC1111y/AL | 630 | 90/3.00 | 38.46 | 38.85 | 32.76 | 2.8 | 6300 | 170 |

y=1 for Black y=2 for Red y=3 for White y=4 for Blue y=5 for Green/Yellow

NB: We may not stock all sizes in all colour variations

Bigger Size available on request

DOMINION CABLES – LIGHTING FIJI AND THE PACIFIC A3

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **CONDUCTOR** | **CURRENT RATING (a)** **Fixed Wiring** | | | **ELECTRICAL CHARACTERISTICS** | | | |
| **Nominal Area**  **mm2** | **Unenclosed In Air**  **2SINGLEA**  **A** | **Conduit**  **In Air**  **2SINLEDA**  **A** | | **Maximum**  **DC**  **Resistance @20°C**  **Ω/km** | **Maximum**  **AC**  **Resistance @90°C**  **Ω/km** | **Equivalent Star Reactance**  **(trefoil)**  **Ω/km** | **Single Phase Voltage Drop**  **(trefoil)**  **@90°C**  **mV/Am** |
| 1 | 13 | | 13 | 21.2 | 27.0 | 0.168 | 54.1 |
| 1.5 | 16 | | 18 | 13.6 | 17.3 | 0.157 | 34.7 |
| 2.5 | 23 | | 24 | 7.41 | 9.45 | 0.143 | 18.9 |
| 4 | 31 | | 32 | 4.61 | 5.88 | 0.137 | 11.8 |
| 6 | 40 | | 41 | 3.08 | 3.93 | 0.128 | 7.87 |
| 10 | 54 | | 54 | 1.83 | 2.33 | 0.118 | 4.68 |
| 16 | 72 | | 70 | 1.15 | 1.47 | 0.111 | 2.95 |
| 25 | 97 | | 94 | 0.727 | 0.927 | 0.106 | 1.87 |
| 35 | 119 | | 112 | 0.524 | 0.668 | 0.101 | 1.35 |
| 50 | 146 | | 138 | 0.387 | 0.494 | 0.0962 | 1.01 |
| 70 | 184 | | 170 | 0.268 | 0.342 | 0.0917 | 0.710 |
| 95 | 230 | | 212 | 0.193 | 0.247 | 0.0904 | 0.528 |
| 120 | 267 | | 242 | 0.153 | 0.197 | 0.0870 | 0.431 |
| 150 | 308 | | 282 | 0.124 | 0.160 | 0.0868 | 0.365 |
| 185 | 358 | | 320 | 0.0991 | 0.129 | 0.0862 | 0.311 |
| 240 | 428 | | 381 | 0.0754 | 0.0991 | 0.0847 | 0.262 |
| 300 | 495 | |  | 0.0601 | 0.0803 | 0.0839 | 0.233 |
| 400 | 577 | |  | 0.0470 | 0.0646 | 0.0829 | 0.211 |
| 500 | 668 | |  | 0.0366 | 0.0525 | 0.0820 | 0.196 |
| 630 | 770 | |  | 0.0283 | 0.0432 | 0.0800 | 0.184 |

(a) Based on 40**°**C ambient air temperature.

The above information is from the following sources: AS/NZS 3008.1.1:2009 (tables 4, 30, 34, 40)

AS 1125:2001 (table 2.3)

For installation with thermal insulation refer to AS/NZS 3008 for de-rating factors.

Do not put in direct contact with polystyrene, polyurethane or similar thermal insulation materials.

***DOMINION WIRE & CABLES LTD.***

# QUALITY CABLE MANUFACTURES, DISTRIBUTORS AND EXPORTERS

**LOT 3, KINGS ROAD, YALALEVU, BA. P.O. BOX 1562, BA, FIJI.**

## PHONE: (679)6675244 FAX: (679)6670023,

## E-Mail: [sales@dominioncables.com](mailto:sales@dominioncables.com) Web: www.dominioncables.com

**Dominion Cables is a leader in the Cable Industry. The services of sales and technical staff are always available to assist with any enquiry.**

**The Dominion Cables policy is one of continual improvement. Details as published may be subject to change.**

This brochure is distributed with the understanding that the authors and editors are not responsible for the results of any action taken on the basis of information in this work, or any errors or omissions. Further, Dominion Cables is not engaged in rendering professional services. Dominion Cables expressly disclaims all and any liability to any person in respect of anything and of the consequences of anything done or omitted to be done by any such person in reliance whether whole or partial of the whole or any part of the contents of this publication. All rights reserve

DOMINION CABLES – LIGHTING FIJI AND THE PACIFIC A4