FLAT TPS

2C + E

COPPER

## APPLICATION

Easi-peel sheath for general wiring unenclosed, enclosed in conduit, buried direct or in underground ducts for domestic, commercial and industrial installations where not subject to mechanical damage.

STANDARD	AS/NZS 5000.2

VOLTAGE	450/750V

CONDUCTOR	Copper 1 - 16mm2

INSULATION	PVC, V-90

Red, Black & Green/Yellow

SHEATH	PVC, 3V-90

White

MAX. OPERATING TEMP.	90 °C

| Item Number | Conductor |  | Overall Diameter | Approx. Mass kg/km | Minimum Installed Bending Radius mm |
| --- | --- | --- | --- | --- | --- |
|  | mm2 | (No./mm) | Nominal mm |  |  |
| DC309 | 1 | 1/1.13 | 4.5 x 9.5 | 85 | 55 |
| DC329 | 1.5 | 7/0.50 | 4.7 x 10.2 | 115 | 65 |
| DC339 | 2.5 | 1/1.78 | 5.8 x 12.0 | 140 | 70 |
| DC349 | 2.5 | 7/0.67 | 5.5 x 12.4 | 150 | 75 |
| DC359 | 4 | 7/0.85 | 6.5 x 14.0 | 220 | 85 |
| DC369 | 6 | 7/1.04 | 7.1 x 15.2 | 270 | 95 |
| DC379 | 10 | 7/1.35 | 8.5 x 18.6 | 440 | 115 |
| DC389 | 16 | 7/1.70 | 10.0 x 21.3 | 500 | 130 |

DOMINION CABLES – LIGHTING FIJI AND THE PACIFIC                                                                                                       A15   A11

| CONDUCTOR | CURRENT RATING (a) |  |  | ELECTRICAL CHARACTERISTICS |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Area mm2 | Unenclosed In Air A | Surrounded by thermal insulation A | Buried In Ducts A | Maximum DC Resistance @20°C /km | Maximum AC Resistance @90°C /km | Equivalent Star Reactance /km | Single Phase Voltage Drop mV/Am |
| 1 (1/1.13) | 14 | 7 | 17 | 21.2 | 27.0 | 0.119 | 54.1 |
| 1.5 (7/0.50) | 18 | 9 | 21 | 13.6 | 17.3 | 0.111 | 34.7 |
| 2.5 (7/0.67) | 26 | 13 | 30 | 7.41 | 9.45 | 0.102 | 18.9 |
| 2.5 (1/1.78) | 26 | 13 | 30 | 7.28 | 9.45 | 0.102 | 18.9 |
| 4 (7/0.85) | 34 | 17 | 39 | 4.61 | 5.88 | 0.102 | 11.8 |
| 6 (7/1.04) | 44 | 22 | 50 | 3.08 | 3.93 | 0.0967 | 7.85 |
| 10 (7/1.35) | 60 | 30 | 66 | 1.83 | 2.33 | 0.0906 | 4.68 |
| 16 (7/1.70) | 80 | 40 | 114 | 1.15 | 1.47 | 0.0861 | 2.95 |

(a) Based on 40°C ambient air temperature and where applicable, burial depth of 0.5m, soil temperature of 25°C and soil resistivity of 1.2°C.m/W.

The above information is from the following sources:		AS/NZS 3008.1.1:2009 (tables 10, 30, 35, 42)

AS 1125:2001 (table 2.3)

For installation with thermal insulation refer to AS/NZS 3008 for de-rating factors.

Do not put in direct contact with polystyrene, polyurethane or similar thermal insulation materials.

| ACTIVE / CONDUCTOR |  |  | EARTH CONDUCTOR |  |  |
| --- | --- | --- | --- | --- | --- |
| Nominal Area mm2 | Nominal Diameter mm | Min Insulation Thickness mm | Nominal Area mm2 | Number & Diameter of Wires No/mm | Min Insulation Thickness mm |
| 1 (1/1.13) | 1.1 | 0.6 | 1.0 | 7/0.50 | 0.6 |
| 1.5 (7/0.50) | 1.5 | 0.6 | 1.5 | 7/0.50 | 0.6 |
| 2.5 (7/0.67) | 2.0 | 0.7 | 2.5 | 7/0.67 | 0.7 |
| 2.5 (1/1.78) | 1.8 | 0.7 | 2.5 | 7/0.67 | 0.7 |
| 4 (7/0.85) | 2.5 | 0.8 | 2.5 | 7/0.67 | 0.7 |
| 6 (7/1.04) | 3.1 | 0.8 | 2.5 | 7/0.67 | 0.7 |
| 10 (7/1.35) | 3.9 | 1.0 | 4.0 | 7/0.85 | 0.8 |
| 16 (7/1.70) | 4.9 | 1.0 | 6.0 | 7/1.04 | 0.8 |

DOMINION WIRE & CABLES LTD.

# QUALITY CABLE MANUFACTURES, DISTRIBUTORS AND EXPORTERS

LOT 3, KINGS ROAD, YALALEVU, BA. P.O. BOX 1562, BA, FIJI.

## PHONE: (679)6675244  FAX: (679)6670023,

## E-Mail: sales@dominioncables.com		Web: www.dominioncables.com

Dominion Cables is a leader in the Cable Industry. The services of sales and technical staff are always available to assist with any enquiry.

The Dominion Cables policy is one of continual improvement. Details as published may be subject to change.

This brochure is distributed with the understanding that the authors and editors are not responsible for the results of any action taken on the basis of information in this work, or any errors or omissions. Further, Dominion Cables is not engaged in rendering professional services. Dominion Cables expressly disclaims all and any liability to any person in respect of anything and of the consequences of anything done or omitted to be done by any such person in reliance whether whole or partial of the whole or any part of the contents of this publication. All rights reserve

DOMINION CABLES – LIGHTING FIJI AND THE PACIFIC                                                                                                         A16